SECTION 212200 – CLEAN AGENT FIRE EXTINQUISHING SYSTEMS

GENERAL

SECTION INCLUDES

Piping and piping specialties.

Extinguishing agent container(s) and distribution components.

Extinguishing agent.

Control and supervisory systems.

Manual pull, clean agent release and abort stations.

Clean agent audible and visual notification devices.

Air sampling smoke detection system.

Air sampling smoke detection pipe distribution network.

Connection devices for and wiring between components.

Connection devices for power and integration into building systems.

Alarm operation description.

Trouble operation description.

Signs and identification.

RELATED SECTIONS

Revise SECTION AND ASSOCIATED NUMBERS in subparagraphS below to meet project requirements.

Section [01 33 23]: Shop Drawings, Product Data, and Samples.

DEFINITIONS

AHJ	Authority Having Jurisdiction.

ASSD	Air Sampling Smoke Detection.

BAS	Building Automation System.

FM	Factory Mutual.

FPE 	Fire Protection Engineer.

HVAC	Heating, Ventilation and Air Conditioning.

PE	Professional Engineer.

NAC	Notification Appliance Circuit.

NFPA	National Fire Protection Association.

NICET	National Institute for Certification in Engineering Technologies.

NRTL	Nationally Recognized Testing Laboratory.

SCP	Suppression Control Panel.

SFD	Standard Fire Detection.

UL	Underwriters Laboratory.

VEWFD	Very Early Warning Fire Detection.

SCOPE

This specification outlines the requirements for engineering a “Total Flood” clean agent fire extinguishing system with automatic detection and control. The work described in this specification includes all design, engineering, labor, materials, equipment and services necessary and required, to complete and test the clean agent fire extinguishing and control system. The clean agent fire extinguishing and control system shall be an engineered system for total flooding of a Modular Data Center as indicated in Section [01 33 23].

Although such work is not specifically indicated, furnish and install all supplementary or miscellaneous items, appurtenances, switches and devices necessary for a sound, secure and complete installation in full compliance with all applicable codes and requirements of the local Authorities Having Jurisdiction (AHJ).

APPLICABLE STANDARDS AND PUBLICATIONS

The design, equipment, installation, testing and maintenance of the Viking Clean Agent Suppression System shall be in accordance with the applicable requirements set forth in the latest edition of the following codes and standards.

NFPA 2001 - Clean Agent Fire Extinguishing Systems.

NFPA 70 - National Electric Code.

NFPA 72 – National Fire Alarm and Signaling Code.

[NFPA 75:	Standard for the Fire Protection of Information Technology Equipment.]

[NFPA 76:	Standard for the Fire Protection of Telecommunication Facilities.]

FM - Factory Mutual Approval Guide.

UL - Fire Protection Equipment Directory.

Department of Transportation (DOT) Title 49 Code of Federal Regulations.

NEMA – Enclosures for Industrial Controls and Systems.

All Requirements of Authority Having Jurisdiction (AHJ).

The standards listed, as well as all other applicable codes, standards, and good engineering practices shall be used as "minimum" design standards.

REQUIREMENTS

The Suppression System installation shall be made in accordance with the drawings, specifications and applicable standards. Should a conflict occur between the drawings and specifications, the specifications shall prevail.

Exclusions

The work listed below shall be provided by others, or under other sections of this specification:

120 VAC or 220 VAC power supply to the system control panel.

Interlock wiring and conduit for shutdown of HVAC, dampers and/or electric power supplies, relays or shunt trip breakers.

Connection to local/remote fire alarm systems or listed central alarm station(s).

QUALITY ASSURANCE

MANUFACTURER

The manufacturer of the clean agent fire extinguishing system hardware shall be Viking Corporation.  (No Substitution Allowed).

The name of the manufacturer Viking shall appear on all major clean agent fire extinguishing system components.

All devices, components and equipment shall be the products pre-engineered designed and integrated by the clean agent fire extinguishing system manufacturer, whether directly manufactured or not.

All devices, components and equipment shall be new, standard products of the latest design and suitable to perform the functions intended.

All devices and equipment shall be UL Listed and/or FM Approved.

INSTALLER

The installing contractor shall be trained by the system manufacturer to design, install, test and maintain clean agent extinguishing system, including all related components.

When possible, the installing contractor shall employ a NICET certified special hazard designer, Level III or above, who will be responsible for this project.

The installing contractor shall be an experienced firm regularly engaged in the installation of automatic Clean Agent, or similar, fire suppression systems in strict accordance with all applicable codes and standards.

The installing contractor must have a minimum of five (5) years’ experience in the design, installation and testing of Clean Agent, or similar, fire suppression systems. A list of systems of a similar nature and scope shall be provided on request.

The installing contractor shall show evidence that his company carries a minimum $2,000,000.00 liability and completed operations insurance policy. These limits shall supersede limits required in the general conditions of the specifications.

The installing contractor shall maintain, or have access to, a Clean Agent recharging station. The installing contractor shall provide proof of this ability to recharge the largest Clean Agent system within 24-hours after a discharge including the amount of bulk agent storage available.

The installing contractor shall be an authorized stocking distributor of the Clean Agent system equipment so that immediate replacement parts are available from inventory.

The installing contractor shall show proof of emergency service available on a twenty-four-hour-a-day, seven-day-a-week basis.

SUBMITTALS

Submittals shall be in full compliance with the requirements of NFPA 72, Chapter 7, 2016 Edition.

The installing contractor shall submit the following design information and drawings for approval prior to starting installation on this project:

            - Working plans indicating detailed layout of system, locating each component (e.g. agent cylinder, control panel, air sampling smoke detector, sampling holes, electric/manual pull station, audible and visual alarms). Include control diagrams, wiring diagrams, written sequence of operation or cause and affect matrix along with battery calculations, and pipe locations including size and length. Refer to NFPA  2001.

            - Product data for each piece of equipment comprising the system, including storage cylinders, control valves and pilot controls, control panels, nozzles, manual stations, air sampling smoke detectors, alarm bells or horns, switches, and annunciators.

            - Design calculations derived from the VSH “DesignManager” computer program VSH1230 Module and verified by both Underwriters Laboratories and Factory Mutual. Analysis shall include calculations to verify system terminal pressures, nozzle flow rates, orifice code number, piping pressure losses, component flow data, and pipe sizes considering actual and equivalent lengths of pipe and elevation changes. Designers using this software shall be trained and certified by Viking Corporation. Software shall allow for 87% of the agent in the pipe distribution network.

            - Design calculation derived from ASSD pipe modeling program. Analysis shall include calculations to verify transport time, sample hole sensitivity, suction pressure, balance and share.

            - Manufacturer's installation and operation manuals.

          - Submit drawings, calculations and system component data sheets for approval to the local fire prevention agency, owner’s insurance underwriter, and all other authorities having jurisdiction before starting installation. Submit approved plans to the architect/engineer for record.

SYSTEM REQUIREMENTS

SYSTEM DESCRIPTION AND OPERATION

The clean agent extinguishing system shall be a be a Viking VSH1230 Total Flooding System utilizing 3M Novec 1230 fluid at 360 psi. The system shall utilize a conventional agent release detection and control system, be equipped with an air sampling smoke detector cross-zoned with an appropriate number of photoelectric spot-type smoke detectors, and shall include all discharge nozzles, pipe and fittings, manual release and abort stations, audible and visual alarm devices, auxiliary devices and controls, shutdowns, alarm interface, caution/advisory signs, functional checkout and testing, training and all other operations necessary to form a complete and functional system. The system shall be supplied by Viking SupplyNet. (No Exceptions).

Viking SupplyNet

(800) 968-9501

All wiring related to the clean agent extinguishing system shall be in conduit.

The system shall provide a minimum agent design concentration of 4.5% by volume for Class A and C hazards, in all areas within the protected space. Complete clean agent discharge shall be within 10 seconds and maintain a minimum 4.5% concentration by volume at the anticipated temperature for a MINIMUM of 10-minute holding time within the protected space or greater as determined by the zone integrity fan testing per Annex C of NFPA-2001. Such factors as unclosable openings (if any), “rundown” time for fans, time required for dampers to close, and all other features of the Modular Data Center shall be considered. Concentration may vary depending on the AHJ but may never be less than 4.5% for Class A and Class C hazards.

Locate extinguishing agent supply [and back-up supply] in designated area of Modular Data Center enclosure.

The clean agent extinguishing system design nozzle placement shall be located in a symmetrical or near symmetrical pattern within the protected area. 180 degree nozzles shall be located on the long wall and shall not be located near or in corners of the protected area.  360 degree nozzles are designed to be located on, or near, the centerline of the protected area, discharging toward the perimeter of the area being covered.  The system designers shall layout the nozzles on the floor plan coordinating with all trades and verify the entire area being protected is adequately covered without “Blind Spots” due to nozzle locations.  Nozzle placement within the protected space shall follow the manufacturers design guide recommendations as a minimum.

The following critical areas as a minimum shall be provided with an approved engineered clean agent suppression system for protection of the entire room from structural ceiling to finished floor.  If air containment systems are provided, the space within the containment shall be protected with clean agent suppression system and provided with detection as well.  Reference Section [01 33 23] for all protected areas.

Automatic actuation of the clean agent fire extinguishing system shall include an Air Sampling Smoke Detection (ASSD) system cross-zoned with photoelectric spot-type smoke detector(s).

The ASSD system shall consist of an assembly housing an integral aspiration fan, flow sensor(s), filter, laser based detection chamber, and control, output and supervision circuitry.

The ASSD System shall be powered by a regulated 24 VDC power source provided with backup rechargeable batteries.

The ASSD system shall consist of an air sampling pipe distribution network which shall include piping, tubing, fittings and fasteners as specified herein.  Piping shall originate from the ASSD apparatus and extend to the protected area(s).  Sampling points shall be placed along the air sampling pipe distribution network in accordance with this Specification and Section [01 33 23].  The air sampling pipe distribution network shall be supported by calculations from the Manufacturer’s published pre-engineered design documentation.

In operation, the aspiration fan in the ASSD apparatus draws air from the protected area(s) through sampling holes in the air sampling pipe distribution network then to the ASSD detector assembly where it is analyzed for concentration of fire products.

For detection of smoke concentration within the Modular Data Center:

The ASSD system shall be designed to meet VEWFD criteria.

Provide appropriate number of ASSD apparatuses to efficiently and adequately cover designated area(s).

ASSD apparatus shall be installed in an accessible location and at an accessible height not to exceed 5 ft (1.5 m) as indicated in Section [01 33 23].

Air sampling pipe distribution networks shall be constructed using CPVC pipe mounted to the underside of the ceiling, supported five (5) foot on center and labeled in accordance with NFPA 72 guidelines.

Sampling holes shall be drilled directly into the air sampling pipe distribution network, be oriented downward and be within 4 inches (101mm) below the underside of the ceiling as indicated in Section [01 33 23]. All sampling points shall be marked with the Manufacturer’s standard identification labels as specified herein.

Maximum coverage per sampling hole shall not exceed 200 sq ft (18.5 sq m), exception being where obstructions such as air supply diffusers would otherwise prevent this spacing objective from being met, in which case placement shall be just outside perimeter of obstruction.

Where air containment systems are provided, sampling hole spacing shall be reduced, not to exceed 6 ft (1.8 m) on center.

Sampling holes shall be a minimum of 3ft (1 m) away from air supply diffusers.

Sampling holes shall be installed in an area on the ceiling that is free from obstructions for a minimum of 18 inches (457 mm) on all sides.

Placement of sampling holes nearest to walls shall be greater than 12 inches (304mm) and not exceed 7 ft (2 m) within open areas, or 3 ft (1 m) within air containment systems when present.

Transport time from further sampling hole on each pipe or pipe branch shall not exceed 60 seconds.

Sampling hole balance shall be equal to or greater than 70%.

ASSD apparatuses shall exhaust into an equal or lessor pressure and in no case shall the Δp between ASSD apparatuses sampling pipe(s) and detector exhaust exceed 100 Pa (0.4 inches of water).

The “Alert” threshold shall be programmed with a 15 second delay and set to achieve the equivalent of 0.20% obs/ft (0.64% obs/m) at each sampling hole (VEWFD).

The “Fire 1” threshold shall be programmed with a 30 second delay and set to achieve the equivalent of 2.5% obs/ft (8.0% obs/m) at each sampling hole (SFD).

ASSD airflow fault monitoring shall be programmed with a 60 second delay.

ASSD filter fault reminder feature shall be programmed for 1825 days.

Where local codes and standards dictate placement and spacing of sampling holes that is more stringent than those specified herein, local codes and standards shall prevail.

Release initiation of the clean agent fire extinguishing system shall incorporate “AND” logic, requiring an “Alert” and “Fire 1” threshold relay on the ASSD system and one or more photoelectric spot-type smoke detectors be actuated at the same time. THE “ALERT”, FIRE 1 THRESHOLD OR SPOT-TYPE SMOKE DETECTOR(S) SHALL NEVER ON ITS OWN DIRECTLY INITIATE RELEASE OF THE AGENT.

Automatic operation of protected area(s) shall be as follows:

Actuation of ASSD “Alert” threshold and/or alarm from one or more photoelectric spot-type smoke detector(s) shall:

Energize the “Alert” threshold LED and relay on the activated ASSD detector.

Flash the COMMON ALARM lamp and corresponding zone lamp on the control panel face.

Display “Pre-Alarm” on the control panel LCD.

Energize an alarm AGENT horn device in coded fashion (1 second on, 1 second off) for first stage.

Transfer auxiliary contacts which can perform auxiliary system functions such as:

- Operate door holder/closures on access doors.

- Transmit a signal to a building fire alarm system, if present.

- Shutdown HVAC equipment.

Signal the building fire alarm control panel or BAS, where provided, reporting a pre-alarm condition.

Actuation of ASSD “Fire 1” threshold in addition to one or more photoelectric spot-type smoke detector(s) shall:

Energize the “Fire 1” threshold LED and relay on the activated ASSD detector.

Flash the PRE-DISCHARGE lamp on the control panel face and annunciator.

Energize a pre-discharge AGENT horn device in a coded fashion ½ second on, ½ second off) for 2nd stage alarm stage and activate strobe device in hazard.

Shut down the HVAC system and/or dampers.

Start time-delay sequence (not to exceed 60 seconds).

System abort sequence is enabled at this time.

Signal the building fire alarm control panel or BAS, where provided, reporting a suppression release initiation condition.

After completion of the time-delay sequence, the cylinder electric actuator shall activate, the Clean Agent system shall discharge and the following shall occur:

Illuminate the “DISCHARGE” lamp on the control panel face.

Shutdown of all power to high-voltage equipment.

Energize a strobe-visual indicator(s) outside the hazard in which the discharge occurred.

Energize an “AGENT” horn-audible tone steady.

Activate electric actuator.

Signal the building fire alarm control panel or BAS, where provided, reporting a suppression release has occurred.

The system shall be capable of being actuated by manual discharge devices located at each hazard exit. Operation of a manual device shall duplicate the sequence description above except the time delays and abort functions shall be bypassed. The manual discharge station shall be of the electrical actuation type and shall be supervised at the agent release control panel.

Activation of ASSD or spot-type smoke detector fault condition shall:

Energize the “Trouble” LED on the ASSD detector.

Energize the “Trouble” LED on the affected spot-type smoke detector(s).

Energize the “Trouble” relay on the ASSD detector.

Illuminate the “Trouble” lamp on the control panel face.

Signal the building fire alarm control panel or BAS, where provided, reporting a supervisory detector fault condition.

Reference Section [01 33 23] for connectivity, interaction and function between other systems and devices.

MATERIALS AND EQUIPMENT

GENERAL REQUIREMENTS

The VSH1230 Clean Agent System materials and equipment shall be standard products of the supplier’s latest design and suitable to perform the functions intended. When one or more pieces of equipment must perform the same function(s), they shall be duplicates produced by one manufacturer.

All devices and equipment shall be UL Listed and/or FM approved.

The fire suppression agent shall be Novec 1230 fire protection fluid; clean dry, non-corrosive, non-damaging, non-deteriorating, and meeting the requirements of NFPA 2001. The agent shall be suitable for use in normally occupied spaces. Agent shall be listed as “Acceptable” on the EPA’s SNAP list.

CLEAN AGENT STORAGE AND DISTRIBUTION

Each system shall have its own supply of clean agent.

The system design can be modular, central storage, or a combination of both design criteria.

Systems shall be designed in accordance with the manufacturer’s guidelines.

Each supply shall be located within the hazard area, or as near as possible, to reduce the amount of pipe and fittings required to, install the system.

The clean agent shall be stored in Viking Agent Storage Cylinder Assemblies. Cylinders shall be super-pressurized with dry nitrogen to an operating pressure of 360 psi @ 70°F (24.8 bar @ 20°C). Cylinders shall be of high-strength low alloy steel construction and conform to NFPA 2001.

Cylinders shall have a threaded protection ring on the tank collar and ¼” steel protection cap for handling and shipment.

Valve shall be constructed of forged brass and operate by means of pressure differential. Valve shall be constructed as to not require rebuild after discharge, Valve shall allow for means to pressurize cylinder without need for valve operation.

The primary cylinder assembly(s) shall be actuated by a resettable electric actuator or by pneumatic means from a PAE pilot cylinder. Non-resettable or explosive devices shall not be permitted.

All solenoids shall be supervised by a Solenoid Monitor Switch. Viking part number 922290D & 922291D.

The cylinders shall be mounted using wall racks on solid walls. The cylinders and racks shall be arranged to allow a service aisle for cylinder removal and cylinder weighing.

Each cylinder assembly shall have a contact pressure gauge with integrated low pressure switch to provide visual and electrical supervision of the cylinder pressure. The low pressure switch shall be wired to the control panel to provide an audible and visual supervisory condition signal in the event the cylinder pressure drops below 10% working pressure. The pressure gauge shall be color coded to provide an easy, visual indication of cylinder pressure.

Each cylinder assembly shall have a pressure relief provision that automatically operates before the internal pressure exceeds 710 psi (49 bar).

When more than one cylinder is connected to a common manifold, a check valve shall be provided with each cylinder.

Engineered discharge nozzles shall be provided within the manufacturer’s guidelines to distribute the Novec 1230 fluid throughout the protected spaces. The nozzles shall be designed to provide proper agent quantity and distribution. Nozzles shall be available in ½ in. through 2 in. pipe sizes. Each size shall be available in 180°and 360º distribution patterns.

Nozzles shall be permanently marked as to part number and orifice diameter.

Nozzles shall be of the type utilizing internal orifice plates.

Nozzles shall be shall be approved for an extended effective nozzle height of 17.9 feet.

180° Nozzles shall have 35.77 ft. radius of coverage.

Back to back 180° nozzles shall be approved for installation.

Nozzle flow rate shall be capable of 476 pounds.

System vertical tank to nozzle height shall be capable of 53.8’ feet.

If nozzles are only located above the tank outlet, then the maximum elevation difference between the tank and outlet and the furthest horizontal pipe run or discharge nozzle (whichever is furthest) shall not exceed 53.8 ft.

If nozzles are only located below the tank outlet, then the maximum elevation difference between the tank and outlet and the furthest horizontal pipe run or discharge nozzle (whichever is furthest) shall not exceed 53.8 ft.

If nozzles are only located above and below the tank outlet, then the maximum

elevation difference between the discharge nozzles shall not exceed 53.8 ft.

Distribution piping, and fittings, shall be installed in accordance with the manufacturer’s requirements, NFPA 2001 and approved piping standards and guidelines. All distribution piping shall be installed by qualified individuals using accepted practices and quality procedures. All piping shall be adequately supported and anchored at all directional changes and nozzle locations. The piping shall be laid out to give maximum flow and to avoid possible mechanical, chemical or other damage. Installation shall follow drawings as closely as possible. System designer must be consulted for anything other than minor deviations in pipe routing.

Black or galvanized steel pipe shall be either ASTM A53 seamless or electric welded, Grade A or B or ASTM A-106, Grade A, B, or C. ASTM A-120, ordinary cast-iron pipe, aluminum pipe, or non-metallic pipe shall not be used. Stainless steel pipe shall be 304, 316, 304L, or 316L for threaded connections or 304L or 316L for welded connections.

Threaded fittings must comply with NFPA 2001 and be at a minimum class 300 malleable iron, class 300 ductile iron. Cast iron and Class 150 pound fittings shall not be used.

Grooved fittings and couplings must comply with NFPA 2001. Piping shall be rolled or cut grooved in accordance with the fitting or coupling manufacturer's guidelines.

Gaskets must be compatible with Novec 1230 fluid (typically EPDM having a temperature range of -30°F to 230°F [-34°C to 110°C]). Gasket lubricant must be in accordance with manufacturer's specifications.

The minimum allowable working pressure at 70°F (21.1°C) for pipe and fittings in closed sections of pipe must be greater than or equal to the maximum operating pressure of the discharge pipe safety relief valve.

Reductions in pipe sizes may be accomplished using threaded or grooved concentric reducing fittings, steel or stainless steel concentric swage fittings, or steel or stainless steel reducing bushings. All such fittings must comply with NFPA 2001. Pipe reductions can be made using machined or forged steel hex bushings. Malleable and/or cast iron bushings are NOT to be used.

All piping shall be reamed, blown clear and swabbed with suitable solvents to remove burrs, mill varnish and cutting oils before assembly.

All screwed pipe shall be coated with Teflon tape.

Piping shall be pneumatically tested in a closed circuit for a period of 10 minutes at 40 psi (2.76 bar) per the latest edition of NFPA 2001. At the end of 10 minutes, the pressure drop shall not exceed 20 percent of the test pressure. The pressure test shall be permitted to be omitted if the total piping contains no more than one change in direction fitting between the storage container and the discharge nozzle, and where all piping is physically tested for tightness.

AGENT RELEASE CONTROL PANEL

The agent release control panel shall be a conventional-type and its components shall be UL Listed and/or FM Approved for release.

The agent release control panel shall perform all functions necessary to operate the system detection, actuation and auxiliary functions as outlined.

The agent release control panel shall be capable of providing standby power for a minimum duration of 24-hours of standby and 5-minutes in alarm, or as required to meet local jurisdictional requirements.

The agent release control panel shall support Cross-Zoned, Single Detector Release and Manual Release detection/actuation methods.

The agent release control panel shall provide the following capabilities and functions:

The Control Panel shall include six programmable initiating device circuits, four programmable output circuits, three programmable Form-C relays, a minimum of 4.0 Amp integral power supply, a minimum of 1.0 Amp auxiliary power output, and an LCD for user interface.

The IDCs (Initiating Device Circuits) shall be individually programmable as conventional two-wire smoke detector circuits, as well as any dry contact input device. The IDCs shall support Style D (Class A) operations by adding an expansion board. The IDCs shall support conventional two-wire smoke detectors as well as conventional smoke detectors capable of generating a maintenance signal when the detector becomes dirty and a separate supervisory ‘freeze’ signal when ambient temperature falls below the detector rating of approximately 45 degrees F.

The four programmable outputs shall be individually programmable as conventional supervised NACs (Notification Appliance Circuits) or for releasing solenoids. Each NAC may be individually programmed as any of the following: Silence Inhibit, Auto-Silence, Strobe Synchronization, Selective Silence (horn-strobe mute), Temporal or Steady Signal, Silenceable or Non-silenceable, or Release Stage Sounder. The system shall also provide resettable and non-resettable output power for general use.

The agent release control panel shall be capable of coding Notification Appliance Circuits in March Time Code (120 PPM), Temporal (NFPA 72), and California Code, Main panel notification circuits (NACs 1,2,3 & 4) shall also automatically synchronize any of the following manufacturer’s notification appliances connected to them: System Sensor, Wheelock, Gentex, Faraday and Amseco, with no need for additional synchronization modules.

The three programmable relays shall be individually programmable as Alarm, Trouble, Supervisory, Discharge, and AC Power Loss.  When programmed as a Trouble relay, the relay shall be fail-safe.

The on board power supply shall be capable of 4.0 Amps minimum of regulated, filtered power.

AIR SAMPLING SMOKE DETECTOR (ASSD):

The ASSD apparatus shall be aspirated laser-based mass light scattering type and capable of detecting a wide range of smoke particle types of varying size.  A particle counting method shall be employed for the purposes of:

Preventing large particles from affecting the true smoke reading.

Monitoring contamination of the filter (dust & dirt etc.) to automatically notify when maintenance is required.  The particle counting method shall not be used for the purpose of smoke density measurement.

Be equipped with an integral two-stage disposable filter cartridge.  The first stage shall be capable of filtering particles in excess of 20 microns from the air sample.  The second stage shall be ultra-fine, removing more than 99% of contaminant particles of 0.3 microns or larger, to provide a clean air barrier across critical detector optics to eliminate internal detector contamination.

Be self-monitoring for filter contamination and provide indication through system fault when replacement is necessary.  Detectors which allow automatic reset of filter status upon removal and reinsertion are not permitted.

Contain relays for alarm and fault conditions.  The relays shall be software programmable to the required functions.

Be equipped with a general purpose input to allow either: Remote Reset, Isolate or Standby.

Be provided with an integral display featuring indicator LED’s and control buttons.

Permit configuration by programmers that are either integral to the system, portable or PC based.

Allow configuration of:

Smoke threshold alarm levels.

Time and date.

Time delays.

Faults, including airflow, detector, power, filter and network as well as an indication of the urgency of the fault.

Relay outputs for remote indication of alarm and fault conditions.

General purpose input functionality.

Simulated electronic testing of relays.

Provide a minimum of two alarm output levels corresponding to Alert and Fire 1.  Alarm levels shall be programmable and able to be set within listed limits at absolute sensitivities meeting sensitivity objectives specified herein.

Incorporate a flow sensor in each pipe inlet and provide staged airflow faults.  Detector units which permit unsupervised disabling of flow sensors is not permitted.

Incorporate facilities to transmit the following faults:

Detector

Airflow

Filter

System

Zone

Network

Power

Urgent and Minor faults

Store internally a minimum of 18,000 events in its history buffer for future extraction and analysis of events and operational status.

AIR SAMPLING PIPE NETWORK, FITTINGS AND MOUNTING HARDWARE:

Material for sampling pipe and associated fittings shall be in accordance with local codes and standards.

Pipe inside diameter shall be in accordance with Manufacturer’s guidelines.

Pipe interior shall be smooth bore.

Pipe shall be labeled as per local codes and standards.

All fittings shall be made with compatible pre-formed elbows, tees, couplings, end caps and unions.

All joints in the sampling pipe must be air tight and made by using compatible solvent cement, except at entry to the detector.

Mechanical pipe fasteners and hangers shall be approved for use with the pipe material in which it is supporting.  Fasteners and hangars shall allow pipe to freely slide in and out to facilitate expansion and contraction of the material.

It shall be the installing contractor’s responsibility to confirm pipe and tubing material and mounting methods selected meets this Specification and requirements of the local AHJ.

MANUAL RELEASE (ELECTRIC)

The electric manual release station shall be a dual action device which provides a means of manually discharging the clean agent fire extinguishing system when used in conjunction with the agent release control panel.

The manual release station shall be Viking P/N 16656.

The manual release station shall be a dual action device requiring two distinct operations to initiate a system actuation.

The manual release station shall bypass the time delay and abort functions, shall cause the system to discharge and shall cause all release and shutdown devices to operate in the same manner as if the system had operated automatically.

A manual release station shall be located at each exit from the protected hazard

MANUAL RELEASE (MECHANICAL)

Mechanical Manual Release shall be made available in the event all battery back-up and commercial power is lost. Viking P/N 887668 Manual Release shall be installed atop the electric actuator. Consideration should be given for convenience of operation and egress from the hazard area(s).

ABORT STATION

The Abort Station shall be “Dead Man” type and shall be located next to each manual release station.

“Locking” or “Keyed” abort stations shall not be permitted.

The Abort Station shall be Viking P/N 17120.

AUDIBLE and VISUAL ALARMS

Audible alarm and visual signal devices shall operate from the RP-2002 Control Panel.

Alarms shall operate on 24 VDC nominal polarized.

Audible alarms shall provide continuous or interrupted tones with an output sound level of at least 90 dBA measured at 10 feet from the device.

A Strobe device shall be placed outside, and above, each exit door.

BATTERIES

Shall be 12.0 volt, Gel-Cell type (2 required) and sized according to provide sufficient standby power as specified herein.

Battery shall have sufficient capacity to power the fire alarm system for not less than 24-hours plus 5-minutes of alarm upon a normal AC power failure or as required to meet local jurisdictional requirements.

The batteries are to be completely maintenance free.

ELECTRICAL INSTALLATION

Installation shall be in accordance with the NFPA 70 (NEC), NFPA 72, NFPA 2001, local and state codes, as shown on the drawings, and as recommended by the major equipment manufacturer.

All conduit, junction boxes, conduit supports and hangers shall be concealed in finished areas and may be exposed in unfinished areas. Conduit installation shall be in accordance with The National Electrical Code (NEC), local and state requirements. Smoke detectors shall not be installed prior to the system programming and test period. If construction is ongoing during this period, measures shall be taken to protect smoke detectors from contamination and physical damage.

All fire detection and alarm system devices, control panels and remote annunciators shall be surface mounted.

DOCUMENTATION AND TESTING

SYSTEM INSPECTION AND CHECKOUT

After the system installation has been completed, the entire system shall be checked out, inspected and functionally tested by qualified, trained personnel, in accordance with the manufacturer’s recommended procedures and NFPA standards.

All containers and distribution piping shall be checked for proper mounting and installation.

All electrical wiring shall be tested for proper connection, continuity and resistance to earth.

The complete system shall be functionally tested, in the presence of the owner or his representative, and all functions, including system and equipment interlocks, must be operational at least five (5) days prior to the final acceptance tests.

Each detector shall be tested in accordance with the manufacturer’s recommended procedures, and test values recorded.

All system and equipment interlocks, such as door release devices, audible and visual devices, equipment shutdowns, local and remote alarms, etc. shall function as required and designed.

Each control panel circuit shall be tested for trouble by inducing a trouble condition into the system.

TRAINING REQUIREMENTS

Prior to final acceptance, the installing contractor shall provide operational training to each shift of the owner’s personnel. Each training session shall include control panel operation, manual and abort functions, trouble procedures, supervisory procedures, auxiliary functions and emergency procedures.

OPERATION AND MAINTENANCE

Prior to final acceptance, the installing contractor shall provide complete operation and maintenance instruction manuals, four (4) copies for each system, to the owner. All aspects of system operation and maintenance shall be detailed, including piping isometrics, wiring diagrams of all circuits, a written description of the system design, sequence of operation and drawing(s) illustrating control logic and equipment used in the system. Checklists and procedures for emergency situations, troubleshooting techniques, maintenance operations and procedures shall be included in the manual.

AS-BUILT DRAWINGS

Upon completion of each system, the installing contractor shall provide four (4) copies of system “As-Built” drawings to the owner. The drawings shall show actual installation details including all equipment locations (e.g. control panel(s), agent container(s), detectors, alarms, manuals and aborts, etc.) as well as piping and conduit routing details. Show all room or facilities modifications, including door and/or damper installations completed.

ACCEPTANCE TESTS

At the time “As-Built” drawings and maintenance/operations manuals are submitted, the installing contractor shall submit a “Test Plan” describing procedures to be used to test the control system(s). The Test Plan shall include a step-by-step description of all tests to be performed and shall indicate the type and location of test apparatus to be employed. The tests shall demonstrate that the operational and installation requirements of this specification have been met. All tests shall be conducted in the presence of the owner and shall not be conducted until the Test Plan has been approved.

The tests shall demonstrate that the entire control system functions as designed and intended. All circuits shall be tested: automatic actuation, solenoid and manual actuation, HVAC and power shutdowns, audible and visual alarm devices and manual override of abort functions. Supervision of all panel circuits, including AC power and battery power supplies, shall be tested and qualified.

If required, a room pressurization test shall be conducted, in each protected space, to determine the presence of openings which would affect the agent concentration levels. The test(s) shall be conducted using the Door Fan system with integrated computer program. All testing shall be in accordance with NFPA 2001.

If room pressurization testing indicates that openings exist which would result in leakage and/or loss of the extinguishing agent, the installing contractor shall be responsible for coordinating the proper sealing of the protected space(s) by the general contractor or his sub-contractor or agent. The general contractor shall be responsible for adequately sealing all protected space(s) against agent loss or leakage. The installing contractor shall inspect all work to ascertain that the protected space(s) have been adequately and properly sealed. THE SUPPRESSION SYSTEM INSTALLING CONTRACTOR SHALL BE RESPONSIBLE FOR THE SUCCESS OF THE ROOM PRESSURIZATION TESTS. If the first room pressurization test is not successful, in accordance with these specifications, the installing contractor shall direct the general contractor to determine, and correct, the cause of the test failure. Copies of successful test results shall be submitted to the owner for record. Upon acceptance by the owner, the completed system(s) shall be placed into service.

SYSTEM INSPECTIONS

The installing contractor shall provide two (2) inspections of each system, installed under this contract, during the one-year warranty period. The first inspection shall be at the six-month interval, and the second inspection at the 12-month interval, after system acceptance. Inspections shall be conducted in accordance with the manufacturer’s guidelines and the recommendations of NFPA 2001.

Documents certifying satisfactory system(s) operation shall be submitted to the owner upon completion of each inspection.

WARRANTY

All components furnished and installed under this contract shall be warranted against defects in design, materials and workmanship for the full warranty period which is standard with the manufacturer, but in no case less than one (1) year from the date of system acceptance.

END OF SECTION 21 22 00